[image: image1.emf] 

[image: image2.emf] 

[image: image3.png]UNITED ENERGY



[image: image4.emf] 

[image: image5.png]Wl
AusNet

services




VICTORIAN ELECTRICAL DISTRIBUTION NETWORKS (VEDN)
Underground Electrical Infrastructure Auditor Checklist:  OPEN TRENCH - Civil 
This audit is to be conducted prior to the installation of cables and is only for the civil works.

	Project Network #
	
	Drawing #
	

	Project Name
	

	Location
	

	Project Type
	 FORMCHECKBOX 
 Network Managed Project
	 FORMCHECKBOX 
 Customer Managed Project

	
	 FORMCHECKBOX 
 Residential 
	 FORMCHECKBOX 
 Residential 

	
	 FORMCHECKBOX 
 Industrial/Commercial
	 FORMCHECKBOX 
 Industrial/Commercial

	
	 FORMCHECKBOX 
 Public Lighting 
	 FORMCHECKBOX 
 Public Lighting 

	PROJECT SCOPE (Brief description eg:  10 Pits, 150m of Trench, 6 P/L poles)

	

	Network Project Manager 
	

	Location. 
	
	Phone No
	
	Email
	

	

	Customer Project Manager 
	

	Location.
	
	Phone No
	
	Email
	

	

	Electrical Constructor 
	

	Contact
	
	Phone No
	
	Email
	

	

	Civil Contractor
	

	VEDN  No.
	
	Phone No
	
	Email
	

	

	Worksite Auditor/s

	

	VEDN No.
	
	Phone No
	
	Email
	

	

	Network Auditor
	

	 VEDN No.
	
	Phone No
	
	Email
	

	

	Cable Detailer


	

	
	
	Phone No
	
	Email
	

	

	Network Auditor
	

	Phone No.
	
	Mobile No
	
	Email
	

	

	ASSESSMENT DETAILS

	Initiator
	
	Audit Date
	

	Position
	
	Auditor 
	

	Company
	
	Company
	


	INSPECTION ITEM GUIDELINES
	Comp

y/n/na
	Date
	Initials
	Comments

	DESIGN SPECIFICATION

	Approved construction drawing provided (current)
	
	
	
	

	SITE REFERENCES

	Lot title boundaries pegged
	
	
	
	

	Kerb & channel installation complete
	
	
	
	

	Final surface levels can be determined
	
	
	
	

	TRENCH  

	WIDTH - To design specification eg. shared use
	
	
	
	

	DEPTH -  Compliant with plan and final surface level
	
	
	
	

	OFFSET - Alignment correct
	
	
	
	

	DEVIATION - No unapproved route deviations 
	
	
	
	

	JOINT HOLES – correct size
	
	
	
	

	BEDDING SAND  

	Correct depth when compacted  (min 50mm)
	
	
	
	

	Correct grade/type   
	
	
	
	

	Free of rocks, sharp or foreign objects
	
	
	
	

	SERVICE PITS

	Location – correct boundaries 
	
	
	
	

	Entry conduits installed (75mm  +/- 25 mm into pit)
	
	
	
	

	Body not distorted, lid fitted & operational
	
	
	
	

	CONDUITS 

	Correct size and category  
	
	
	
	

	DEPTH -  Compliant with plan and final surface level
	
	
	
	

	Road crossing – Telco separation (100mm LV & 300mm HV) incl. tape 
	
	
	
	

	Separation to other utilities (as specified by Network Owner)
	
	
	
	

	Road crossing – extension past BOK & stormwater
	
	
	
	

	All  conduits capped or sealed and no internal grit or rubble
	
	
	
	

	Warning tape installed (300mm  +/- 50mm from final ground level)
	
	
	
	

	AS BUILT DETAILS

	Assets details recorded prior to cover/backfill 
	
	
	
	

	Supporting digital photographs recorded/attached
	
	
	
	

	Provide Name  and Company responsible                  (Recognised Cable Detailer)
	

	SUBSTATION RESERVE (Where specified) 

	Free of all other authorities’ underground assets
	
	
	
	

	Site flat and level 
	
	
	
	

	Substation site dimensions as per  Technical Standard  
	
	
	
	

	If specified: retaining wall, batter & drainage installed
	
	
	
	

	Foundation culvert installed and level as per Technical Standard
	
	
	
	

	Foundation located correctly within substation site  
	
	
	
	


	Photographs showing compliance and non-compliance items are to be attached


	NOTES  (Attach extra sheets as required)

	

	

	

	

	

	

	

	

	

	

	

	Note: All non-compliances must be rectified or variations approved by Network Owner Project Manager prior to submission of the completed Civil and Electrical Open Trench Audit Report.

	DECLARATION

	The above project -:

 FORMCHECKBOX 
 complies

 FORMCHECKBOX 
 does not comply

with all relevant Network Technical Standards and approved drawings at the time of audit inspection.  
(Tick as applicable)

	Approved Worksite Civil or Electrical or Network Auditor

	Audited by
	
	VEDN No.
	

	Signature
	
	Date
	


VEDN Checklist Open Trench – Civil Audit V6

21/09/2015

[image: image1.emf][image: image2.emf][image: image3.png][image: image4.emf][image: image5.png]